- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ASTM A126, Specification for Grey Iron Castings for Valves, Flanges and Pipe Fittings.

      - ASTM A216 / 216, Specification for Steel Castings, Carbon, Suitable for Fusion Welding for High-Temperature Service.

      - ASTM A278, Specification for Grey Iron Castings for Pressure - Containing Parts for Temperatures up to 345(C.

      - ASTM A351 / A351, Specification for Steel Castings, Austenitic, for High-Temperature Service.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM A47M, Specification for Ferrite Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black, and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.25, Butt welding Ends.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI/ASME B18.2.2, Square and Hex Nuts.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PARTIE 2 – PRODUITS

  - Braided Metal Flexible Connectors

    - Interior component consist of a stainless steel accordion tube.

    - Exterior sheathing consists of a stainless steel braided mesh.

    - Diameter and end connections: as indicated on drawings.

    - Maximum working pressure: 1034 kPa (150 psi).

    - Maximum working temperature: 93°C (200°F).

    - Acceptable component:

      - 2”  and less: Flo Fab series ST;

      - 2-1/2” and larger: Flo Fab series SM.

  - Anchors and pipe supports

    - Anchors.

      - As indicated;

      - Concrete and metal reinforcement: as prescribed.

    - Pipe guide.

      - Provided by the manufacturer of the piping.

      - Agree to the thickness of insulation required over the piping.

      - Design to preserve the integrity of the vapour barrier and pipe liner.

    - Acceptable component: Flo Fab series PG.

- PART 3 – EXECUTION

  - Installation

    - Install flexible connectors in a room temperature environment. Record the values when placing item under pressure and temperature.

    - Install flexible connector according to manufacturer's instructions.

    - Once installed, the flexible connector will be able to absorb a lateral displacement of 150 mm (5.9"). The ratio between the length of the flexible part and the diameter of the connector must not be less than 6 and the length of hose must not exceed 600 mm (23-5/8").

End of Section