- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - National Plumbing Code of Canada.

      - ASTM A126, Specification for Grey Iron Castings for Valves, Flanges and Pipe Fittings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ANSI / AWWA C700, Cold Water Meters - Displacement Type.

      - ANSI / AWWA C701, Cold Water Meters - Turbine Type for Customer Service.

      - ANSI / AWWA C702, Cold Water Meters - Compound Type.

      - CAN / CSA – B64 Séries 7, Backflow Preventers and Vacuum Breakers.

      - CAN / CSA-B64.10, Selection and Installation of Backflow Preventers/Maintenance and Field Testing of Backflow Preventers.

      - CAN3-B79, Commercial and residential drains and cleanouts.

      - CSA-B356-00 UPD 3, Water Pressure Reducing Valves for Domestic Water Supply Systems.

      - PDI - G101, Testing and Rating Procedure for Grease Interceptors with Appendix of Sizing and Installation Data.

      - PDI - WH201, Water Hammer Arrestors.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Strainer

    - Strainer body casted in a “Y” profile with detachable screen.

    - For piping up to and including 2”:

      - Bronze body conforming to ASTM B-62 or cast iron as per ASTM A-278M class 30. Maximum working pressure 2758 kPa (400 psi) and maximum working temperature 66(C (150(F).

      - Connection: Threaded.

      - Screen : Stainless Steel mesh containing 0.8 mm (1/32") preforations;

      - Strainer contains provision for Blow Off of screen mesh;

      - Acceptable component: Flo Fab series LBTY et LCTY.

    - For piping including and above 2-½”:

      - Cast iron body as per ASTM A-278M class 30. Maximum working pressure 1034 kPa (150 psi) and maximum working temperature 66(C (150(F).

      - Connection: Flanged.

      - Screen: Stainless Steel

        - 2-½” to 12” : mesh with 1.2 mm (3/64") perforations.

        - 14” to 16” : mesh with 3.18 mm (1/8") perforations.

      - Strainer contains provision for Blow Off of screen mesh.

      - Acceptable component: Flo Fab series LYF.

- PART 3 – EXECUTION

  - Installation

    - Installation shall conform to National Plumbing Code of Canada and any other local laws and regulations.

    - Install strainers allowing sufficient space to perform regular removal and maintanence of the screen and is correctly oriented, arrow embossed on body indictes direction of flow.

    - Start-up:

        - Ensure that the screen is easily accessible;

        - Do not proceed with the start-up unless all of the deficiencies have been identified and corrected;

        - Clean screens repeatedly after the initial start-up until the all physical contamination is removed from the liquid medium.

End of Section