- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

  - Submittals

    - Product Data:

      - Submit dimensional drawings and technical data in conformance with client’s instructions.

      - Submit pump performance curve indicating point of operation.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Vertical-in-Line and/or Horizontal Pump Positions

    - Volute: Cast Iron Class 30 (ASTM No. A 159), suction and discharge side flanged connections. Threaded connections for pressure gauges at the inlet and discharge flanges, for venting and draining, and for optional thermometer. The pump casing is a UNIVERSAL design to allow several different piping installations.  Incorporated in the volute casting is a solid base with four anchor holes for vertical installations position.  The pump casing and motor shall have a steel base plate if installed in a horizontal position. Servicing of the pump in vertical or horizontal positions without disturbing the piping connections.The volute includes a wear ring that is replaceable. Maximum operating pressure is 1200 kPa (175 psi).

    - Impeller: Cast Bronze (ASTM No. B 584), closed type, dynamically balanced, keyed to the stainless steel shaft and secured by a stainless steel bolt and washer.

    - Shaft: stainless steel, fitted with bronze sleeve and butane O-ring.

    - Sealing: The wet-end components are sealed with a self-lubricating mechanical seal. The seal is composed of a ceramic seat, a rotating carbon ring, a viton bellow and all other materials in stainless steel. It is designed for continuous operation at maximum working temperature of 400°F (205°C) corresponding to a maximum working pressure of 1724 kPa (250 psi).

    - Coupling: Pumps above 5HP - A flexible coupling of steel hubs and rubber sleeve between the pump and motor shaft located inside a “power frame”, permitting the servicing of the pump; mechanical seal, wear ring, impeller, without disturbing the piping connections. Servicing of the pump without disturbing the piping connections in both vertical or horizontal positions. NO coupling alignment is required as motor and pump is self aligned.

.

    - Motor: respecting the requirements of Section 15010. Motor and pump are designed for vertical and/or horizontal mounting. Motors equipped with grease lubricated heavy duty ball bearings, suitable for maximum loads created by the pump. Motor type TC or T, high-efficiency class B with a safety factor of 1.15 for series XRI.

    - Selection of motor will allow the pump to operate at maximum capacity without surpassing the maximum amperage draw on the motor.

    - Each pump is hydrostatically tested.

    - Size and Capacity: As specified on pump tables shown on [plans] [specifications].

    - Acceptable component: Flo Fab series XRI.

- PART 3 – EXECUTION

  - General Installation of Vertical-in-line and/or Horizontal position.

    - Vertical Mount pumps so that the fluid flows in the direction indicated by the arrow engraved on the body, that grease nipples are easily accessible and once power is applied to the motor that the impeller in rotating in the correct direction. NO coupling alignment is required as motor and pump is self aligned.

    - Horizontal Mount Pumps mounted on base: providing templates for determining the location of anchor bolts and sleeves, level pump by utilizing the necessary shims and encase the base cement. NO coupling alignment is required as motor and pump is self aligned.  Arrow engraved on the pump body for the flow directions, and once power is applied to the motor that the impeller in rotating in the correct direction

    - Install support elements or piping hangers such that the body of the pump does not support the any piping or equipment. Refer to details and installation instructions from the manufacturer.

    - Install a valve and piping between the drain connection on the pump volute and the floor drain.

    - Install a valve to be able to release entrapped air in the volute.

    - Install valves in conjunction with pressure gauges.

End of Section