- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME, Section VIII, Boiler and Pressure Vessel Code (BPVC).

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A278M, Specification for Gray Iron Castings for Pressure-Containing Parts for Temperatures up to 345°C.

      - ASTM A516 / 516M, Specification for Pressure Vessel Plates, Carbon Steel, for Moderate and Lower Temperature Service.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B51, Boiler, pressure vessel, and pressure piping code.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, a type, series or model number reference, year constructed, pressure ;

      - All details relating to the operation, and the care and maintenance;

- PART 2 – PRODUCT

Combination Air and Sediment Separators:

Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model ADSF (fixed) or ADSF-HV (fixed high velocity) or comparable product by the following:

Tank: Welded steel; ASME constructed and labeled for 125-psig (860-kPa) minimum working pressure and 250 deg F (121 deg C) maximum operating temperature.

Coalescing Medium: Stainless steel.

End Inlet and Outlet Connections: Threaded for NPS 2 (DN 50) and smaller; flanged connections for NPS 2-1/2 (DN 65) and larger.

Vent Connection: Threaded.

Blowdown Connection: Threaded.

Skim Valve Connection: Threaded.

Head: Non-Removable.

Size: Match system flow capacity.

Vertical base.

- PART 3 – EXECUTION

  - Installation

    - Install accessories in accordance with the PID schematic and as recommended by the manufacturer. Ensure connection of all purge fittings to the closest floor drains.

    - Provide sufficient clearance for access to equipment for maintenance. If the final location should be different from that indicated on the schematics, then consult the owner before proceeding with the installation.

    - Refer to installation drawings supplied by the manufacturer.

    - If there is insufficient clearances then advise the owner and comply with his directives.

    - Check and adjust the pressure before starting the system, it must correspond to the fill system pressure or the “cut-in” start pressure.

End of Section