- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - CAN1 - 4.1, Water heater gas accumulation which are below the maximum heat 75,000 Btu / h.

      - CAN1 - 4.3, Water heater gas flow, gas water heater instantaneous water heaters and large automatic gas storage.

      - CAN / CGA - B149.1, Natural gas installation code.

      - CAN / CGA - B149.2, Propane installation code.

      - CSA B51, Vessel code and Pressure Piping.

      - CAN/CSA - B139, Installation code for oil burning equipment.

      - CAN / CSA - B140.0, General Requirements for Oil Burning Equipment

      - CSA B140.12, Domestic water heaters and pool heating oil.

      - CAN / CSA C22.2 n( 110, Construction and testing of storage electric water heaters.

      - CAN / CSA - C191 Series, CSA Standards on Performance of Electric Storage Tank Water Heaters (Functional standards on water heaters electric storage).

      - CAN / CSA - C309, Performance Requirements for Glass-Lined Storage Tanks for Household Hot Water Service.

      - B.N.Q. 3560.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCTS

Furnish and install, as shown on plans, a PF______________ as manufactured by Flo Fab Inc.

The tank shall incorporate a chemical fill basin with a minimum dimension of 6” to help facilitate complete introduction of required solutions. The tank shall be constructed for 200 psi working pressure and 450°F. The chemical feed tank must be constructed in accordance with most recent addendum of Section VII Division 1 of the ASME Boiler and Pressure Vessel Code.

Each tank shall be Flo Fab model number PF______________ or approved equal.

    - 1 year standard warranty on the tank.

    - Features :

      - Capacity: 	[____] litres ([____] gal US).

      - Tank size (as indicated) [____] mm diameter x [____] mm long ([____] inch diameter x [____] inch in length).

    - Acceptable product: Flo Fab Series PF

- PARTIE 3 – EXÉCUTION

  - Installation

    - Install the tank according to manufacturer's recommendations and requirements of applicable codes and authorities.

    - Cradles are used for receiving the tank upright. These cradles are each deposited on a concrete pad to provide a clearance of 200 mm between them and the ground

    - Supply and install structural steel elements required for assembly of tanks.

    - Provide a drain valve piped to nearest floor drain.

    - The tank should be equipped with a safety valve, with pressure and temperature ASME certified, factory installed.

    - Provide the electrical connection under Section 16 of the spec.

End of section